ARCGIS ONLINE FEATURE REPORT

LPGBS SITE SURVEY

Inspection dossier template - auto-generated from the Survey123 Connect XLSForm. Yes/No questions render as live checkbox glyphs and repeat groups print as iterating tables.

| Site | ${loc_city}, ${loc_state} (${loc_id}) |
| --- | --- |
| Facility Type | ${fac_type} |
| JCN / JON | ${jcn} / ${jon} |
| Address | ${address} |
| County / Service Area | ${county} / ${service_area} |
| Report Generated | ${$feature ¦ getValue:"" ¦ format:"MM/DD/YYYY hh:mm a"} |
| Survey Version | ${survey_version} |
| XLSForm Version | 2.1 |

Filled checkboxes (☒) represent the recorded answer for each question. Empty boxes (☐) indicate an unselected option.

| 1.0 | FACILITY DATA AND DESKTOP INSPECTION |
| --- | --- |

|  | Project Name ${project_name}; JCN ${jcn}; JON ${jon}. Address ${address}; City ${loc_city}; State ${loc_state}. County ${county}; Service Area ${service_area}; ATCT Level/Tier ${atct_tier}. Year Built ${year_built}; Tower Owner ${tower_owner}; Is this a FAA-owned tower? ${faa_owned ¦ checked:"yes"} Yes ${faa_owned ¦ checked:"no"} No ${faa_owned ¦ checked:"n/a"} N/A. If this is a non-FAA-owned tower, obtain the lease document ${lease_document}; Are there LPGBS drawings available? ${drawings_available ¦ checked:"yes"} Yes ${drawings_available ¦ checked:"no"} No ${drawings_available ¦ checked:"n/a"} N/A. Obtain exterior lightning protection system drawing. ${# ext_lightning_protect_drawing}${$file ¦ size:0:0:560:380}${/}. Obtain earth electrode system (EES) drawing. ${# ees_drawing}${$file ¦ size:0:0:560:380}${/}. Obtain interior electronic ground drawing. ${# int_elect_grounding_drawing}${$file ¦ size:0:0:560:380}${/}. Obtain electrical one-line drawing with surge protective devices. ${# elect_one_line_drawing}${$file ¦ size:0:0:560:380}${/}. If drawing available, look up height info and enter drawing reference # ${height_reference_drawing}; ATCT Height ${atct_height}; Height measured from ground level to ${height_measured_from}. If drawing available, look up sides info and enter drawing reference # ${sides_reference_drawing}; # of Sides of ATCT Building ${tower_sides}. Is the facility a standalone ATCT or with attached base building or integrated with airport structure. ${standalone_atct ¦ appearance:"multiline"}. Is TRACON facility attached to the ATCT ${tracon_attached ¦ checked:"yes"} Yes ${tracon_attached ¦ checked:"no"} No ${tracon_attached ¦ checked:"n/a"} N/A. What is the ATCT building exterior/panel material. ${building_exterior_material ¦ checked:"Concrete"} Concrete ${building_exterior_material ¦ checked:"AluminumPanels"} Aluminum Panels. Function of cable chases ${cable_chase_function}; Number of cable chases ${number_cable_chases}; Is there a roof-top ASDE ${rooftop_asde ¦ checked:"yes"} Yes ${rooftop_asde ¦ checked:"no"} No ${rooftop_asde ¦ checked:"n/a"} N/A. Survey Version ${survey_version}. |
| --- | --- |

| 1.1 | Survey Information |
| --- | --- |

|  | Location. ${location}. LOC ID. ${loc_id}. Fac Type. ${fac_type}. Form Type ${form_type ¦ checked:"Streamlined"} Streamlined ${form_type ¦ checked:"Guided"} Guided. Survey Elements. ${survey_elements ¦ checked:"Gate_Fence"} Gate/Fence ${survey_elements ¦ checked:"EES"} EES ${survey_elements ¦ checked:"Tower"} Tower ${survey_elements ¦ checked:"Base_Building"} Base Building ${survey_elements ¦ checked:"UPS_Building"} UPS Building ${survey_elements ¦ checked:"UPS_Room"} UPS Room ${survey_elements ¦ checked:"EG_Building"} EG Building ${survey_elements ¦ checked:"EG_Outdoors"} EG Outdoors ${survey_elements ¦ checked:"EG_Room"} EG Room ${survey_elements ¦ checked:"Other"} Other. Provide a general description of the tower site. ${site_description ¦ appearance:"multiline"}. General Photos. ${# general_photos}${$file ¦ size:0:0:560:380}${/}. |
| --- | --- |

| 1.2 | Site Contact Information |
| --- | --- |

|  | Name ${dm_name}; Title ${dm_title}; Email ${dm_email}. Phone ${dm_phone}; Date Contacted ${dm_contacted_date ¦ format:"MM/DD/YYYY"}; Team Member Who Made Contact ${dm_who_contacted}. Name ${fm_name}; Title ${fm_title}; Email ${fm_email}. Phone ${fm_phone}; Date Contacted ${fm_contacted_date ¦ format:"MM/DD/YYYY"}; Team Member Who Made Contact ${fm_who_contacted}. Name ${tm_name}; Title ${tm_title}; Email ${tm_email}. Phone ${tm_phone}; Date Contacted ${tm_contacted_date ¦ format:"MM/DD/YYYY"}; Team Member Who Made Contact ${tm_who_contacted}. Name ${esu_name}; Title ${esu_title}; Email ${esu_email}. Phone ${esu_phone}; Date Contacted ${esu_contacted_date ¦ format:"MM/DD/YYYY"}; Team Member Who Made Contact ${esu_who_contacted}. |
| --- | --- |

REPEAT RECORDS - SURVEY PARTICIPANTS

| ${# SURVEY_PARTICIPANTS} |  |
| --- | --- |
| RECORD ${$position} ¦ Survey Participants |  |
| Field | Response |
| Details |  |
| Select List Name | ${list_name} |
| Name | ${name} |
| Title | ${title} |
| Organization | ${organization} |
| Phone | ${phone} |
| ${/} |  |

| 2.0 | GATES AND FENCE GROUNDING |
| --- | --- |

REPEAT RECORDS - GATES AND FENCE GROUNDING INSPECTION

| ${# GATES_FENCE_GROUNDING} |  |
| --- | --- |
| RECORD ${$position} ¦ Gates and Fence Grounding Inspection |  |
| Field | Response |
| Details |  |
| Describe the Location | ${gfg_location_description} |
| 8.0 Is there a fence around the facility? | ${fence_present ¦ checked:"yes"} Yes ${fence_present ¦ checked:"no"} No |
| Gates and Fence General Photos | ${# gates_fence_images}${$file ¦ size:0:0:560:380}${/} |
| Gates and Fence General Notes | ${gates_fence_general_notes ¦ appearance:"multiline"} |
| Gates and Fence General Issues | ${gates_fence_general_issues ¦ appearance:"multiline"} |
| Gates and Fence Grounding - 8.1 |  |
| 8.1 Are gates bonded to the adjacent posts with flexible 4/0 or copper braided straps( 1" x 1/8")? | ${gfg_bonded_to_posts ¦ checked:"yes"} Yes ${gfg_bonded_to_posts ¦ checked:"no"} No ${gfg_bonded_to_posts ¦ checked:"n/a"} N/A |
| 8.1 Photo | ${# gfg_bonded_to_posts_photo}${$file ¦ size:0:0:560:380}${/} |
| 8.1 Findings | ${gfg_bonded_to_posts_note ¦ appearance:"multiline"} |
| 8.1 Recommendations | ${gfg_bonded_to_posts_rec ¦ appearance:"multiline"} |
| Gates and Fence Grounding - 8.2 |  |
| 8.2 Are the gate bonding jumpers made of insulated 4/0 AWG flexible (welding) copper conductors or copper straps (1 inch by 1/8 inch)? | ${gfg_copper_connectors ¦ checked:"yes"} Yes ${gfg_copper_connectors ¦ checked:"no"} No ${gfg_copper_connectors ¦ checked:"n/a"} N/A |
| 8.2 Photo | ${# gfg_copper_connect_photo}${$file ¦ size:0:0:560:380}${/} |
| 8.2 Findings | ${gfg_copper_connect_note ¦ appearance:"multiline"} |
| 8.2 Recommendations | ${gfg_copper_connect_rec ¦ appearance:"multiline"} |
| Gates and Fence Grounding - 8.3 |  |
| 8.3 Is an exothermic weld-type connection used to bond the conductors/straps to the gates/posts? | ${gfg_exo_weld ¦ checked:"yes"} Yes ${gfg_exo_weld ¦ checked:"no"} No ${gfg_exo_weld ¦ checked:"n/a"} N/A |
| 8.3 Photo | ${# gfg_exo_weld_photo}${$file ¦ size:0:0:560:380}${/} |
| 8.3 If not, please describe the bonding method: | ${gfg_bonding_method ¦ appearance:"multiline"} |
| 8.3 Recommendations | ${gfg_exo_weld_rec ¦ appearance:"multiline"} |
| Gates and Fence Grounding - 8.4 |  |
| 8.4 Are the posts on each side of the gates bonded to the ground rod with 4/0 AWG bare copper conductor? | ${gfg_bonded_to_ground ¦ checked:"yes"} Yes ${gfg_bonded_to_ground ¦ checked:"no"} No ${gfg_bonded_to_ground ¦ checked:"n/a"} N/A |
| 8.4 Photo | ${# gfg_bonded_to_ground_photo}${$file ¦ size:0:0:560:380}${/} |
| 8.4 Findings | ${gfg_bonded_to_ground_note ¦ appearance:"multiline"} |
| 8.4 Recommendations | ${gfg_bonded_to_ground_rec ¦ appearance:"multiline"} |
| Gates and Fence Grounding - 8.5 |  |
| 8.5 Are both gate posts ground rods interconnected below ground with 4/0 AWG bare copper conductor? | ${gfg_bonded_below_ground ¦ checked:"yes"} Yes ${gfg_bonded_below_ground ¦ checked:"no"} No ${gfg_bonded_below_ground ¦ checked:"n/a"} N/A |
| 8.5 Photo | ${# gfg_bonded_below_ground_photo}${$file ¦ size:0:0:560:380}${/} |
| 8.5 Findings | ${gfg_bonded_below_ground_note ¦ appearance:"multiline"} |
| 8.5 Recommendations | ${gfg_bonded_below_ground_rec ¦ appearance:"multiline"} |
| Gates and Fence Grounding - 8.6 |  |
| 8.6 Is there a horizontal bare 6 AWG stranded tinned copper conductor threaded through the metal fabric of the gate? | ${gfg_awg_copper ¦ checked:"yes"} Yes ${gfg_awg_copper ¦ checked:"no"} No ${gfg_awg_copper ¦ checked:"n/a"} N/A |
| 8.6 Photo | ${# gfg_awg_copper_photo}${$file ¦ size:0:0:560:380}${/} |
| 8.6 Findings | ${gfg_awg_copper_note ¦ appearance:"multiline"} |
| 8.6 Recommendations | ${gfg_awg_copper_rec ¦ appearance:"multiline"} |
| Gates and Fence Grounding - 8.7 |  |
| 8.7 Is there an adjoining non-FAA-owned fence connected to the existing FAA perimeter fence? If so, is it electrically isolated? | ${gfg_adjoining_fence ¦ checked:"yes"} Yes ${gfg_adjoining_fence ¦ checked:"no"} No ${gfg_adjoining_fence ¦ checked:"n/a"} N/A |
| 8.7 Photo | ${# gfg_adjoining_fence_photo}${$file ¦ size:0:0:560:380}${/} |
| 8.7 Findings | ${gfg_adjoining_fence_note ¦ appearance:"multiline"} |
| 8.7 Recommendations | ${gfg_adjoining_fence_rec ¦ appearance:"multiline"} |
| ${/} |  |

| 3.0 | EARTH ELECTRODE SYSTEM |
| --- | --- |

REPEAT RECORDS - EARTH ELECTRODE SYSTEM INSPECTION

| ${# EARTH_ELECTRODE_SYSTEM} |  |
| --- | --- |
| RECORD ${$position} ¦ Earth Electrode System Inspection |  |
| Field | Response |
| Details |  |
| Choose Facility Location | ${ees_section_selector} |
| Describe the Location | ${ees_location_description} |
| Will a ground resistance test be performed? | ${grt_performed ¦ checked:"yes"} Yes ${grt_performed ¦ checked:"no"} No |
| How many ground resistance tests will be performed? | ${grt_count} |
| EES General Photos | ${# ees_general_photos}${$file ¦ size:0:0:560:380}${/} |
| EES General Notes | ${ees_general_notes ¦ appearance:"multiline"} |
| EES General Issues | ${ees_general_issues ¦ appearance:"multiline"} |
| Ground Resistance Test - Resistance Test 1 |  |
| Z | ${z_distance_1 ¦ checked:"100"} 100 ${z_distance_1 ¦ checked:"200"} 200 |
| Y1 | ${y_probe_1_1} |
| Ohms 1 | ${resistance_1_1} |
| Y2 | ${y_probe_1_2} |
| Ohms 2 | ${resistance_1_2} |
| Y3 | ${y_probe_1_3} |
| Ohms 3 | ${resistance_1_3} |
| Y4 | ${y_probe_1_4} |
| Ohms 4 | ${resistance_1_4} |
| Y5 | ${y_probe_1_5} |
| Ohms 5 | ${resistance_1_5} |
| Y6 | ${y_probe_1_6} |
| Ohms 6 | ${resistance_1_6} |
| Y7 | ${y_probe_1_7} |
| Ohms 7 | ${resistance_1_7} |
| Y8 | ${y_probe_1_8} |
| Ohms 8 | ${resistance_1_8} |
| Y9 | ${y_probe_1_9} |
| Ohms 9 | ${resistance_1_9} |
| Y10 | ${y_probe_1_10} |
| Ohms 10 | ${resistance_1_10} |
| Ground Resistance Test - Resistance Test 2 |  |
| Z | ${z_distance_2 ¦ checked:"100"} 100 ${z_distance_2 ¦ checked:"200"} 200 |
| Y1 | ${y_probe_2_1} |
| Ohms 1 | ${resistance_2_1} |
| Y2 | ${y_probe_2_2} |
| Ohms 2 | ${resistance_2_2} |
| Y3 | ${y_probe_2_3} |
| Ohms 3 | ${resistance_2_3} |
| Y4 | ${y_probe_2_4} |
| Ohms 4 | ${resistance_2_4} |
| Y5 | ${y_probe_2_5} |
| Ohms 5 | ${resistance_2_5} |
| Y6 | ${y_probe_2_6} |
| Ohms 6 | ${resistance_2_6} |
| Y7 | ${y_probe_2_7} |
| Ohms 7 | ${resistance_2_7} |
| Y8 | ${y_probe_2_8} |
| Ohms 8 | ${resistance_2_8} |
| Y9 | ${y_probe_2_9} |
| Ohms 9 | ${resistance_2_9} |
| Y10 | ${y_probe_2_10} |
| Ohms 10 | ${resistance_2_10} |
| Ground Resistance Test - Resistance Test 3 |  |
| Z | ${z_distance_3 ¦ checked:"100"} 100 ${z_distance_3 ¦ checked:"200"} 200 |
| Y1 | ${y_probe_3_1} |
| Ohms 1 | ${resistance_3_1} |
| Y2 | ${y_probe_3_2} |
| Ohms 2 | ${resistance_3_2} |
| Y3 | ${y_probe_3_3} |
| Ohms 3 | ${resistance_3_3} |
| Y4 | ${y_probe_3_4} |
| Ohms 4 | ${resistance_3_4} |
| Y5 | ${y_probe_3_5} |
| Ohms 5 | ${resistance_3_5} |
| Y6 | ${y_probe_3_6} |
| Ohms 6 | ${resistance_3_6} |
| Y7 | ${y_probe_3_7} |
| Ohms 7 | ${resistance_3_7} |
| Y8 | ${y_probe_3_8} |
| Ohms 8 | ${resistance_3_8} |
| Y9 | ${y_probe_3_9} |
| Ohms 9 | ${resistance_3_9} |
| Y10 | ${y_probe_3_10} |
| Ohms 10 | ${resistance_3_10} |
| Ground Resistance Test - Resistance Test 4 |  |
| Z | ${z_distance_4 ¦ checked:"100"} 100 ${z_distance_4 ¦ checked:"200"} 200 |
| Y1 | ${y_probe_4_1} |
| Ohms 1 | ${resistance_4_1} |
| Y2 | ${y_probe_4_2} |
| Ohms 2 | ${resistance_4_2} |
| Y3 | ${y_probe_4_3} |
| Ohms 3 | ${resistance_4_3} |
| Y4 | ${y_probe_4_4} |
| Ohms 4 | ${resistance_4_4} |
| Y5 | ${y_probe_4_5} |
| Ohms 5 | ${resistance_4_5} |
| Y6 | ${y_probe_4_6} |
| Ohms 6 | ${resistance_4_6} |
| Y7 | ${y_probe_4_7} |
| Ohms 7 | ${resistance_4_7} |
| Y8 | ${y_probe_4_8} |
| Ohms 8 | ${resistance_4_8} |
| Y9 | ${y_probe_4_9} |
| Ohms 9 | ${resistance_4_9} |
| Y10 | ${y_probe_4_10} |
| Ohms 10 | ${resistance_4_10} |
| Ground Resistance Test - Resistance Test Statistics |  |
| Average Resistance | ${average_resistance} |
| EES - 7.1 |  |
| 7.1 In prohibited areas, where exothermic weld may not be used, are hydraulically crimped connections employed? | ${ees_crimps ¦ checked:"yes"} Yes ${ees_crimps ¦ checked:"no"} No ${ees_crimps ¦ checked:"n/a"} N/A |
| 7.1 Photo | ${# ees_crimps_photo}${$file ¦ size:0:0:560:380}${/} |
| 7.1 Findings | ${ees_crimps_note ¦ appearance:"multiline"} |
| 7.1 Recommendations | ${ees_crimps_rec ¦ appearance:"multiline"} |
| EES - 7.2 |  |
| 7.2 Does the access well exist? | ${ees_access_well ¦ checked:"yes"} Yes ${ees_access_well ¦ checked:"no"} No ${ees_access_well ¦ checked:"n/a"} N/A |
| 7.2 Photo | ${# ees_access_well_photo}${$file ¦ size:0:0:560:380}${/} |
| 7.2 Number of Access Wells / Findings | ${ees_access_well_note ¦ appearance:"multiline"} |
| 7.2 Recommendations | ${ees_access_well_rec ¦ appearance:"multiline"} |
| EES - 7.4 |  |
| 7.4 Are all connections in access well exothermically bonded? | ${ees_connect_condition ¦ checked:"yes"} Yes ${ees_connect_condition ¦ checked:"no"} No ${ees_connect_condition ¦ checked:"n/a"} N/A |
| 7.4 Photo | ${# ees_connect_condition_photo}${$file ¦ size:0:0:560:380}${/} |
| 7.4 What is the condition of the connections? | ${ees_connect_condition_note ¦ appearance:"multiline"} |
| 7.4 Recommendations | ${ees_connect_condition_rec ¦ appearance:"multiline"} |
| EES - 7.5 |  |
| 7.5 Using 62% “Fall of Potential” method, does the earth electrode system measure 10 ohms or less or as required in the specification? | ${ees_under_10_ohms ¦ checked:"yes"} Yes ${ees_under_10_ohms ¦ checked:"no"} No ${ees_under_10_ohms ¦ checked:"n/a"} N/A |
| 7.5 Photo | ${# ees_under_10_ohms_photo}${$file ¦ size:0:0:560:380}${/} |
| 7.5 Findings | ${ees_under_10_ohms_note ¦ appearance:"multiline"} |
| 7.5 Recommendations | ${ees_under_10_ohms_rec ¦ appearance:"multiline"} |
| ${/} |  |

| 4.0 | TOWER |
| --- | --- |

| 4.1 | Air Terminals |
| --- | --- |

|  | Does the facility have air terminals? ${tower_at ¦ checked:"yes"} Yes ${tower_at ¦ checked:"no"} No. Air Terminal Photos. ${# tower_at_photos}${$file ¦ size:0:0:560:380}${/}. Air Terminal Notes. ${tower_at_general_notes ¦ appearance:"multiline"}. Air Terminal Issues. ${tower_at_general_issues ¦ appearance:"multiline"}. New 1/2 x 24 air terminals ${tower_at_new_at_qty}; Replace missing/broken air terminals ${tower_at_replace_at_qty}; Fix air terminal mast ${tower_at_fix_at_qty}. |
| --- | --- |

| 4.2 | Down Conductors |
| --- | --- |

|  | Does the facility have down conductors? ${tower_dc ¦ checked:"yes"} Yes ${tower_dc ¦ checked:"no"} No. Down Conductor Photos. ${# tower_dc_photos}${$file ¦ size:0:0:560:380}${/}. Down Conductor Notes. ${tower_dc_general_notes ¦ appearance:"multiline"}. Down Conductor Issues. ${tower_dc_general_issues ¦ appearance:"multiline"}. New dc on facility ${tower_dc_new_qty}; Convert existing dc to 4/0 ${tower_dc_convert_to_4_0}; Secure every 3 feet ${tower_dc_secure_3_feet}. Bond dc to lower tower section with exothermic welds ${tower_dc_bond_to_lower}; Add t-style crossover connections where the dc crosses horizontal eq loop ${tower_dc_add_t_cross}; Add new eq loop on handrail and bond to existing dc from air terminals ${tower_dc_new_eq_handrail}. |
| --- | --- |

| 4.3 | Exterior Metallic Objects |
| --- | --- |

|  | Are all exterior metallic objects bonded to EES or bulkhead plate? ${tower_ext_metal ¦ checked:"yes"} Yes ${tower_ext_metal ¦ checked:"no"} No. Exterior Metallic Objects Photos. ${# tower_ext_metal_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Metallic Objects Notes. ${tower_ext_metal_general_notes ¦ appearance:"multiline"}. Exterior Metallic Objects Issues. ${tower_ext_metal_general_issues ¦ appearance:"multiline"}. Hvac ${tower_ext_metal_hvac}; Junction box ${tower_ext_metal_j_box}; Conduit ${tower_ext_metal_conduit}. Doors ${tower_ext_metal_doors}; Service Rack ${tower_ext_metal_serve_rack}; Load bank ${tower_ext_metal_load_bank}. FST ${tower_ext_metal_fst}; Antenna Masts ${tower_ext_metal_ant_mast}; Ob Lights ${tower_ext_metal_ob_light}. Exhaust Stack ${tower_ext_metal_exhaust}; Awning/Metal Structure ${tower_ext_metal_awning}; Vent/Louvers ${tower_ext_metal_vent}. Stairs ${tower_ext_metal_stairs}. |
| --- | --- |

| 4.4 | Exterior Bulkhead Plates |
| --- | --- |

|  | Does the facility have exterior bulkhead plates? ${tower_ext_bulk ¦ checked:"yes"} Yes ${tower_ext_bulk ¦ checked:"no"} No; Are the bulkhead plates correct? ${tower_ext_bulk_correct ¦ checked:"yes"} Yes ${tower_ext_bulk_correct ¦ checked:"no"} No. Exterior Bulkhead Plates Photos. ${# tower_ext_bulk_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Bulkhead Plates Notes. ${tower_ext_bulk_general_notes ¦ appearance:"multiline"}. Exterior Bulkhead Plates Issues. ${tower_ext_bulk_general_issues ¦ appearance:"multiline"}. Plates are undersized, min 1/4" x 4" ${tower_ext_bulk_hvac}; Plates need bonded to EES with 4/0 ${tower_ext_bulk_j_box}; Plates need corrected to double lug terminals ${tower_ext_bulk_conduit}. Plate needs bonds above 90 degree transition ${tower_ext_bulk_doors ¦ checked:"yes"} Yes; Bond ice bridge to bh plate ${tower_ext_bulk_serve_rack ¦ checked:"yes"} Yes; Jumper ice bridge sections with #6 AWG ${tower_ext_bulk_load_bank ¦ checked:"yes"} Yes. |
| --- | --- |

| 5.0 | EXTERIOR BASE BUILDING |
| --- | --- |

| 5.1 | Air Terminals |
| --- | --- |

|  | Does the facility have air terminals? ${bb_at ¦ checked:"yes"} Yes ${bb_at ¦ checked:"no"} No. Air Terminal Photos. ${# bb_at_photos}${$file ¦ size:0:0:560:380}${/}. Air Terminal Notes. ${bb_at_general_notes ¦ appearance:"multiline"}. Air Terminal Issues. ${bb_at_general_issues ¦ appearance:"multiline"}. New 1/2 x 24 air terminals ${bb_at_new_at_qty}; Replace missing/broken air terminals ${bb_at_replace_at_qty}; Fix air terminal mast ${bb_at_fix_at_qty}. |
| --- | --- |

| 5.2 | Down Conductors |
| --- | --- |

|  | Does the facility have down conductors? ${bb_dc ¦ checked:"yes"} Yes ${bb_dc ¦ checked:"no"} No. Down Conductor Photos. ${# bb_dc_photos}${$file ¦ size:0:0:560:380}${/}. Down Conductor Notes. ${bb_dc_general_notes ¦ appearance:"multiline"}. Down Conductor Issues. ${bb_dc_general_issues ¦ appearance:"multiline"}. New dc on facility ${bb_dc_new_qty}; Convert existing dc to 4/0 ${bb_dc_convert_to_4_0}; Secure every 3 feet ${bb_dc_secure_3_feet}. Bond dc to lower tower section with exothermic welds ${bb_dc_bond_to_lower}; Add t-style crossover connections where the dc crosses horizontal eq loop ${bb_dc_add_t_cross}; Add new eq loop on handrail and bond to existing dc from air terminals ${bb_dc_new_eq_handrail}. Install new eq loop on roof ${bb_dc_new_eq_roof}. |
| --- | --- |

| 5.3 | Exterior Metallic Objects |
| --- | --- |

|  | Are all exterior metallic objects bonded to EES or bulkhead plate? ${bb_ext_metal ¦ checked:"yes"} Yes ${bb_ext_metal ¦ checked:"no"} No. Exterior Metallic Objects Photos. ${# bb_ext_metal_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Metallic Objects Notes. ${bb_ext_metal_general_notes ¦ appearance:"multiline"}. Exterior Metallic Objects Issues. ${bb_ext_metal_general_issues ¦ appearance:"multiline"}. Hvac ${bb_ext_metal_hvac}; Junction box ${bb_ext_metal_j_box}; Conduit ${bb_ext_metal_conduit}. Doors ${bb_ext_metal_doors}; Service Rack ${bb_ext_metal_serve_rack}; Load bank ${bb_ext_metal_load_bank}. FST ${bb_ext_metal_fst}; Antenna Masts ${bb_ext_metal_ant_mast}; Ob Lights ${bb_ext_metal_ob_light}. Exhaust Stack ${bb_ext_metal_exhaust}; Awning/Metal Structure ${bb_ext_metal_awning}; Vent/Louvers ${bb_ext_metal_vent}. Stairs ${bb_ext_metal_stairs}. |
| --- | --- |

| 5.4 | Exterior Bulkhead Plates |
| --- | --- |

|  | Does the facility have exterior bulkhead plates? ${bb_ext_bulk ¦ checked:"yes"} Yes ${bb_ext_bulk ¦ checked:"no"} No; Are the bulkhead plates correct? ${bb_ext_bulk_correct ¦ checked:"yes"} Yes ${bb_ext_bulk_correct ¦ checked:"no"} No. Exterior Bulkhead Plates Photos. ${# bb_ext_bulk_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Bulkhead Plates Notes. ${bb_ext_bulk_general_notes ¦ appearance:"multiline"}. Exterior Bulkhead Plates Issues. ${bb_ext_bulk_general_issues ¦ appearance:"multiline"}. Plates are undersized, min 1/4" x 4" ${bb_ext_bulk_hvac}; Plates need bonded to EES with 4/0 ${bb_ext_bulk_j_box}; Plates need corrected to double lug terminals ${bb_ext_bulk_conduit}. Plate needs bonds above 90 degree transition ${bb_ext_bulk_doors ¦ checked:"yes"} Yes; Bond ice bridge to bh plate ${bb_ext_bulk_serve_rack ¦ checked:"yes"} Yes; Jumper ice bridge sections with #6 AWG ${bb_ext_bulk_load_bank ¦ checked:"yes"} Yes. |
| --- | --- |

| 6.0 | EXTERIOR UPS BUILDING |
| --- | --- |

| 6.1 | Air Terminals |
| --- | --- |

|  | Does the facility have air terminals? ${ups_at ¦ checked:"yes"} Yes ${ups_at ¦ checked:"no"} No. Air Terminal Photos. ${# ups_at_photos}${$file ¦ size:0:0:560:380}${/}. Air Terminal Notes. ${ups_at_general_notes ¦ appearance:"multiline"}. Air Terminal Issues. ${ups_at_general_issues ¦ appearance:"multiline"}. New 1/2 x 24 air terminals ${ups_at_new_at_qty}; Replace missing/broken air terminals ${ups_at_replace_at_qty}; Fix air terminal mast ${ups_at_fix_at_qty}. |
| --- | --- |

| 6.2 | Down Conductors |
| --- | --- |

|  | Does the facility have down conductors? ${ups_dc ¦ checked:"yes"} Yes ${ups_dc ¦ checked:"no"} No. Down Conductor Photos. ${# ups_dc_photos}${$file ¦ size:0:0:560:380}${/}. Down Conductor Notes. ${ups_dc_general_notes ¦ appearance:"multiline"}. Down Conductor Issues. ${ups_dc_general_issues ¦ appearance:"multiline"}. New dc on facility ${ups_dc_new_qty}; Convert existing dc to 4/0 ${ups_dc_convert_to_4_0}; Secure every 3 feet ${ups_dc_secure_3_feet}. Bond dc to lower tower section with exothermic welds ${ups_dc_bond_to_lower}; Add t-style crossover connections where the dc crosses horizontal eq loop ${ups_dc_add_t_cross}; Add new eq loop on handrail and bond to existing dc from air terminals ${ups_dc_new_eq_handrail}. Install new eq loop on roof ${ups_dc_new_eq_roof}. |
| --- | --- |

| 6.3 | Exterior Metallic Objects |
| --- | --- |

|  | Are all exterior metallic objects bonded to EES or bulkhead plate? ${ups_ext_metal ¦ checked:"yes"} Yes ${ups_ext_metal ¦ checked:"no"} No. Exterior Metallic Objects Photos. ${# ups_ext_metal_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Metallic Objects Notes. ${ups_ext_metal_general_notes ¦ appearance:"multiline"}. Exterior Metallic Objects Issues. ${ups_ext_metal_general_issues ¦ appearance:"multiline"}. Hvac ${ups_ext_metal_hvac}; Junction box ${ups_ext_metal_j_box}; Conduit ${ups_ext_metal_conduit}. Doors ${ups_ext_metal_doors}; Service Rack ${ups_ext_metal_serve_rack}; Load bank ${ups_ext_metal_load_bank}. FST ${ups_ext_metal_fst}; Antenna Masts ${ups_ext_metal_ant_mast}; Ob Lights ${ups_ext_metal_ob_light}. Exhaust Stack ${ups_ext_metal_exhaust}; Awning/Metal Structure ${ups_ext_metal_awning}; Vent/Louvers ${ups_ext_metal_vent}. Stairs ${ups_ext_metal_stairs}. |
| --- | --- |

| 6.4 | Exterior Bulkhead Plates |
| --- | --- |

|  | Does the facility have exterior bulkhead plates? ${ups_ext_bulk ¦ checked:"yes"} Yes ${ups_ext_bulk ¦ checked:"no"} No; Are the bulkhead plates correct? ${ups_ext_bulk_correct ¦ checked:"yes"} Yes ${ups_ext_bulk_correct ¦ checked:"no"} No. Exterior Bulkhead Plates Photos. ${# ups_ext_bulk_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Bulkhead Plates Notes. ${ups_ext_bulk_general_notes ¦ appearance:"multiline"}. Exterior Bulkhead Plates Issues. ${ups_ext_bulk_general_issues ¦ appearance:"multiline"}. Plates are undersized, min 1/4" x 4" ${ups_ext_bulk_hvac}; Plates need bonded to EES with 4/0 ${ups_ext_bulk_j_box}; Plates need corrected to double lug terminals ${ups_ext_bulk_conduit}. Plate needs bonds above 90 degree transition ${ups_ext_bulk_doors ¦ checked:"yes"} Yes; Bond ice bridge to bh plate ${ups_ext_bulk_serve_rack ¦ checked:"yes"} Yes; Jumper ice bridge sections with #6 AWG ${ups_ext_bulk_load_bank ¦ checked:"yes"} Yes. |
| --- | --- |

| 7.0 | EXTERIOR EG BUILDING |
| --- | --- |

| 7.1 | Air Terminals |
| --- | --- |

|  | Does the facility have air terminals? ${eg_at ¦ checked:"yes"} Yes ${eg_at ¦ checked:"no"} No. Air Terminal Photos. ${# eg_at_photos}${$file ¦ size:0:0:560:380}${/}. Air Terminal Notes. ${eg_at_general_notes ¦ appearance:"multiline"}. Air Terminal Issues. ${eg_at_general_issues ¦ appearance:"multiline"}. New 1/2 x 24 air terminals ${eg_at_new_at_qty}; Replace missing/broken air terminals ${eg_at_replace_at_qty}; Fix air terminal mast ${eg_at_fix_at_qty}. |
| --- | --- |

| 7.2 | Down Conductors |
| --- | --- |

|  | Does the facility have down conductors? ${eg_dc ¦ checked:"yes"} Yes ${eg_dc ¦ checked:"no"} No. Down Conductor Photos. ${# eg_dc_photos}${$file ¦ size:0:0:560:380}${/}. Down Conductor Notes. ${eg_dc_general_notes ¦ appearance:"multiline"}. Down Conductor Issues. ${eg_dc_general_issues ¦ appearance:"multiline"}. New dc on facility ${eg_dc_new_qty}; Convert existing dc to 4/0 ${eg_dc_convert_to_4_0}; Secure every 3 feet ${eg_dc_secure_3_feet}. Bond dc to lower tower section with exothermic welds ${eg_dc_bond_to_lower}; Add t-style crossover connections where the dc crosses horizontal eq loop ${eg_dc_add_t_cross}; Add new eq loop on handrail and bond to existing dc from air terminals ${eg_dc_new_eq_handrail}. Install new eq loop on roof ${eg_dc_new_eq_roof}. |
| --- | --- |

| 7.3 | Exterior Metallic Objects |
| --- | --- |

|  | Are all exterior metallic objects bonded to EES or bulkhead plate? ${eg_ext_metal ¦ checked:"yes"} Yes ${eg_ext_metal ¦ checked:"no"} No. Exterior Metallic Objects Photos. ${# eg_ext_metal_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Metallic Objects Notes. ${eg_ext_metal_general_notes ¦ appearance:"multiline"}. Exterior Metallic Objects Issues. ${eg_ext_metal_general_issues ¦ appearance:"multiline"}. Hvac ${eg_ext_metal_hvac}; Junction box ${eg_ext_metal_j_box}; Conduit ${eg_ext_metal_conduit}. Doors ${eg_ext_metal_doors}; Service Rack ${eg_ext_metal_serve_rack}; Load bank ${eg_ext_metal_load_bank}. FST ${eg_ext_metal_fst}; Antenna Masts ${eg_ext_metal_ant_mast}; Ob Lights ${eg_ext_metal_ob_light}. Exhaust Stack ${eg_ext_metal_exhaust}; Awning/Metal Structure ${eg_ext_metal_awning}; Vent/Louvers ${eg_ext_metal_vent}. Stairs ${eg_ext_metal_stairs}. |
| --- | --- |

| 7.4 | Exterior Bulkhead Plates |
| --- | --- |

|  | Does the facility have exterior bulkhead plates? ${eg_ext_bulk ¦ checked:"yes"} Yes ${eg_ext_bulk ¦ checked:"no"} No; Are the bulkhead plates correct? ${eg_ext_bulk_correct ¦ checked:"yes"} Yes ${eg_ext_bulk_correct ¦ checked:"no"} No. Exterior Bulkhead Plates Photos. ${# eg_ext_bulk_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Bulkhead Plates Notes. ${eg_ext_bulk_general_notes ¦ appearance:"multiline"}. Exterior Bulkhead Plates Issues. ${eg_ext_bulk_general_issues ¦ appearance:"multiline"}. Plates are undersized, min 1/4" x 4" ${eg_ext_bulk_hvac}; Plates need bonded to EES with 4/0 ${eg_ext_bulk_j_box}; Plates need corrected to double lug terminals ${eg_ext_bulk_conduit}. Plate needs bonds above 90 degree transition ${eg_ext_bulk_doors ¦ checked:"yes"} Yes; Bond ice bridge to bh plate ${eg_ext_bulk_serve_rack ¦ checked:"yes"} Yes; Jumper ice bridge sections with #6 AWG ${eg_ext_bulk_load_bank ¦ checked:"yes"} Yes. |
| --- | --- |

| 8.0 | EXTERIOR ENGINE GENERATOR |
| --- | --- |

| 8.1 | Air Terminals |
| --- | --- |

|  | Does the facility have air terminals? ${eeg_at ¦ checked:"yes"} Yes ${eeg_at ¦ checked:"no"} No. Air Terminal Photos. ${# eeg_at_photos}${$file ¦ size:0:0:560:380}${/}. Air Terminal Notes. ${eeg_at_general_notes ¦ appearance:"multiline"}. Air Terminal Issues. ${eeg_at_general_issues ¦ appearance:"multiline"}. New 1/2 x 24 air terminals ${eeg_at_new_at_qty}; Replace missing/broken air terminals ${eeg_at_replace_at_qty}; Fix air terminal mast ${eeg_at_fix_at_qty}. |
| --- | --- |

| 8.2 | Down Conductors |
| --- | --- |

|  | Does the facility have down conductors? ${eeg_dc ¦ checked:"yes"} Yes ${eeg_dc ¦ checked:"no"} No. Down Conductor Photos. ${# eeg_dc_photos}${$file ¦ size:0:0:560:380}${/}. Down Conductor Notes. ${eeg_dc_general_notes ¦ appearance:"multiline"}. Down Conductor Issues. ${eeg_dc_general_issues ¦ appearance:"multiline"}. New dc on facility ${eeg_dc_new_qty}; Convert existing dc to 4/0 ${eeg_dc_convert_to_4_0}; Secure every 3 feet ${eeg_dc_secure_3_feet}. Bond dc to lower tower section with exothermic welds ${eeg_dc_bond_to_lower}; Add t-style crossover connections where the dc crosses horizontal eq loop ${eeg_dc_add_t_cross}; Add new eq loop on handrail and bond to existing dc from air terminals ${eeg_dc_new_eq_handrail}. Install new eq loop on roof ${eeg_dc_new_eq_roof}. |
| --- | --- |

| 8.3 | Exterior Metallic Objects |
| --- | --- |

|  | Are all exterior metallic objects bonded to EES or bulkhead plate? ${eeg_ext_metal ¦ checked:"yes"} Yes ${eeg_ext_metal ¦ checked:"no"} No. Exterior Metallic Objects Photos. ${# eeg_ext_metal_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Metallic Objects Notes. ${eeg_ext_metal_general_notes ¦ appearance:"multiline"}. Exterior Metallic Objects Issues. ${eeg_ext_metal_general_issues ¦ appearance:"multiline"}. Hvac ${eeg_ext_metal_hvac}; Junction box ${eeg_ext_metal_j_box}; Conduit ${eeg_ext_metal_conduit}. Doors ${eeg_ext_metal_doors}; Service Rack ${eeg_ext_metal_serve_rack}; Load bank ${eeg_ext_metal_load_bank}. FST ${eeg_ext_metal_fst}; Antenna Masts ${eeg_ext_metal_ant_mast}; Ob Lights ${eeg_ext_metal_ob_light}. Exhaust Stack ${eeg_ext_metal_exhaust}; Awning/Metal Structure ${eeg_ext_metal_awning}; Vent/Louvers ${eeg_ext_metal_vent}. Stairs ${eeg_ext_metal_stairs}. |
| --- | --- |

| 8.4 | Exterior Bulkhead Plates |
| --- | --- |

|  | Does the facility have exterior bulkhead plates? ${eeg_ext_bulk ¦ checked:"yes"} Yes ${eeg_ext_bulk ¦ checked:"no"} No; Are the bulkhead plates correct? ${eeg_ext_bulk_correct ¦ checked:"yes"} Yes ${eeg_ext_bulk_correct ¦ checked:"no"} No. Exterior Bulkhead Plates Photos. ${# eeg_ext_bulk_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Bulkhead Plates Notes. ${eeg_ext_bulk_general_notes ¦ appearance:"multiline"}. Exterior Bulkhead Plates Issues. ${eeg_ext_bulk_general_issues ¦ appearance:"multiline"}. Plates are undersized, min 1/4" x 4" ${eeg_ext_bulk_hvac}; Plates need bonded to EES with 4/0 ${eeg_ext_bulk_j_box}; Plates need corrected to double lug terminals ${eeg_ext_bulk_conduit}. Plate needs bonds above 90 degree transition ${eeg_ext_bulk_doors ¦ checked:"yes"} Yes; Bond ice bridge to bh plate ${eeg_ext_bulk_serve_rack ¦ checked:"yes"} Yes; Jumper ice bridge sections with #6 AWG ${eeg_ext_bulk_load_bank ¦ checked:"yes"} Yes. |
| --- | --- |

| 9.0 | EXTERIOR OTHER |
| --- | --- |

| 9.1 | Air Terminals |
| --- | --- |

|  | Does the facility have air terminals? ${other_at ¦ checked:"yes"} Yes ${other_at ¦ checked:"no"} No. Air Terminal Photos. ${# other_at_photos}${$file ¦ size:0:0:560:380}${/}. Air Terminal Notes. ${other_at_general_notes ¦ appearance:"multiline"}. Air Terminal Issues. ${other_at_general_issues ¦ appearance:"multiline"}. New 1/2 x 24 air terminals ${other_at_new_at_qty}; Replace missing/broken air terminals ${other_at_replace_at_qty}; Fix air terminal mast ${other_at_fix_at_qty}. |
| --- | --- |

| 9.2 | Down Conductors |
| --- | --- |

|  | Does the facility have down conductors? ${other_dc ¦ checked:"yes"} Yes ${other_dc ¦ checked:"no"} No. Down Conductor Photos. ${# other_dc_photos}${$file ¦ size:0:0:560:380}${/}. Down Conductor Notes. ${other_dc_general_notes ¦ appearance:"multiline"}. Down Conductor Issues. ${other_dc_general_issues ¦ appearance:"multiline"}. New dc on facility ${other_dc_new_qty}; Convert existing dc to 4/0 ${other_dc_convert_to_4_0}; Secure every 3 feet ${other_dc_secure_3_feet}. Bond dc to lower tower section with exothermic welds ${other_dc_bond_to_lower}; Add t-style crossover connections where the dc crosses horizontal eq loop ${other_dc_add_t_cross}; Add new eq loop on handrail and bond to existing dc from air terminals ${other_dc_new_eq_handrail}. Install new eq loop on roof ${other_dc_new_eq_roof}. |
| --- | --- |

| 9.3 | Exterior Metallic Objects |
| --- | --- |

|  | Are all exterior metallic objects bonded to EES or bulkhead plate? ${other_ext_metal ¦ checked:"yes"} Yes ${other_ext_metal ¦ checked:"no"} No. Exterior Metallic Objects Photos. ${# other_ext_metal_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Metallic Objects Notes. ${other_ext_metal_general_notes ¦ appearance:"multiline"}. Exterior Metallic Objects Issues. ${other_ext_metal_general_issues ¦ appearance:"multiline"}. Hvac ${other_ext_metal_hvac}; Junction box ${other_ext_metal_j_box}; Conduit ${other_ext_metal_conduit}. Doors ${other_ext_metal_doors}; Service Rack ${other_ext_metal_serve_rack}; Load bank ${other_ext_metal_load_bank}. FST ${other_ext_metal_fst}; Antenna Masts ${other_ext_metal_ant_mast}; Ob Lights ${other_ext_metal_ob_light}. Exhaust Stack ${other_ext_metal_exhaust}; Awning/Metal Structure ${other_ext_metal_awning}; Vent/Louvers ${other_ext_metal_vent}. Stairs ${other_ext_metal_stairs}. |
| --- | --- |

| 9.4 | Exterior Bulkhead Plates |
| --- | --- |

|  | Does the facility have exterior bulkhead plates? ${other_ext_bulk ¦ checked:"yes"} Yes ${other_ext_bulk ¦ checked:"no"} No; Are the bulkhead plates correct? ${other_ext_bulk_correct ¦ checked:"yes"} Yes ${other_ext_bulk_correct ¦ checked:"no"} No. Exterior Bulkhead Plates Photos. ${# other_ext_bulk_photos}${$file ¦ size:0:0:560:380}${/}. Exterior Bulkhead Plates Notes. ${other_ext_bulk_general_notes ¦ appearance:"multiline"}. Exterior Bulkhead Plates Issues. ${other_ext_bulk_general_issues ¦ appearance:"multiline"}. Plates are undersized, min 1/4" x 4" ${other_ext_bulk_hvac}; Plates need bonded to EES with 4/0 ${other_ext_bulk_j_box}; Plates need corrected to double lug terminals ${other_ext_bulk_conduit}. Plate needs bonds above 90 degree transition ${other_ext_bulk_doors ¦ checked:"yes"} Yes; Bond ice bridge to bh plate ${other_ext_bulk_serve_rack ¦ checked:"yes"} Yes; Jumper ice bridge sections with #6 AWG ${other_ext_bulk_load_bank ¦ checked:"yes"} Yes. |
| --- | --- |

| 10.0 | INTERIOR BASE BUILDING |
| --- | --- |

| 10.1 | Interior MPG System |
| --- | --- |

|  | Does the facility have Main Ground Plate? ${bb_mpg ¦ checked:"yes"} Yes ${bb_mpg ¦ checked:"no"} No; Is it correct? ${bb_mpg_correct ¦ checked:"yes"} Yes ${bb_mpg_correct ¦ checked:"no"} No. Base Building MPG Photos. ${# bb_mpg_photos}${$file ¦ size:0:0:560:380}${/}. Base Building MPG Notes. ${bb_mpg_general_notes ¦ appearance:"multiline"}. Base Building MPG Issues. ${bb_mpg_general_issues ¦ appearance:"multiline"}. Needs label changed ${bb_mpg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${bb_mpg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${bb_mpg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${bb_mpg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${bb_mpg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 10.2 | Supplemental Ground Plate |
| --- | --- |

|  | Does the facility have Supplemental Ground Plate? ${bb_spg ¦ checked:"yes"} Yes ${bb_spg ¦ checked:"no"} No; Is it correct? ${bb_spg_correct ¦ checked:"yes"} Yes ${bb_spg_correct ¦ checked:"no"} No. Base Building SPG Photos. ${# bb_spg_photos}${$file ¦ size:0:0:560:380}${/}. Base Building SPG Notes. ${bb_spg_general_notes ¦ appearance:"multiline"}. Base Building SPG Issues. ${bb_spg_general_issues ¦ appearance:"multiline"}. Needs label changed ${bb_spg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${bb_spg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${bb_spg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${bb_spg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${bb_spg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 10.3 | MPGP |
| --- | --- |

|  | Does the facility have MPGP's? ${bb_mpgp ¦ checked:"yes"} Yes ${bb_mpgp ¦ checked:"no"} No; Base Building MPGP Count ${bb_mpgp_count}; Are they correct? ${bb_mpgp_correct ¦ checked:"yes"} Yes ${bb_mpgp_correct ¦ checked:"no"} No. Base Building MPGP Photos. ${# bb_mpgp_photos}${$file ¦ size:0:0:560:380}${/}. Base Building MPGP Notes. ${bb_mpgp_general_notes ¦ appearance:"multiline"}. Base Building MPGP Issues. ${bb_mpgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${bb_mpgp_label ¦ checked:"yes"} Yes; Undersized ${bb_mpgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${bb_mpgp_to_double_lug ¦ checked:"yes"} Yes. Needs interconnected with 4/0 to MPGP ${bb_mpgp_interconnect ¦ checked:"yes"} Yes; Need to add additional MPGP's ${bb_mpgp_add_count}; Wrong equipment bonded to MPGP ${bb_mpgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 10.4 | SPGP |
| --- | --- |

|  | Does the facility have SPGP's? ${bb_spgp ¦ checked:"yes"} Yes ${bb_spgp ¦ checked:"no"} No; Base Building SPGP Count ${bb_spgp_count}; Are they correct? ${bb_spgp_correct ¦ checked:"yes"} Yes ${bb_spgp_correct ¦ checked:"no"} No. Base Building SPGP Photos. ${# bb_spgp_photos}${$file ¦ size:0:0:560:380}${/}. Base Building SPGP Notes. ${bb_spgp_general_notes ¦ appearance:"multiline"}. Base Building SPGP Issues. ${bb_spgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${bb_spgp_label ¦ checked:"yes"} Yes; Undersized ${bb_spgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${bb_spgp_to_double_lug ¦ checked:"yes"} Yes. Is incorrectly interconnected with the MPG System (remove the interconnections) ${bb_spgp_inter_mpg ¦ checked:"yes"} Yes; Interconnection with Main/Supp needed with 4/0 ${bb_spgp_interconnect ¦ checked:"yes"} Yes; Need to add additional SPGP's ${bb_spgp_add_count}. Wrong equipment bonded to SPGP ${bb_spgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 10.5 | Interior Equipment Bonding |
| --- | --- |

|  | Does the facility have equipment that needs bonded to the MPG System? ${bb_eqp_bonds ¦ checked:"yes"} Yes ${bb_eqp_bonds ¦ checked:"no"} No; How many? ${bb_eqp_bonds_count}; Is the equipment bonded to the MPG System? ${bb_eqp_bond_mpg ¦ checked:"yes"} Yes ${bb_eqp_bond_mpg ¦ checked:"no"} No. How many? ${bb_eqp_bond_mpg_count}. Base Building Equipment Bonding Photos. ${# bb_eqp_photos}${$file ¦ size:0:0:560:380}${/}. Base Building Equipment Bonding Notes. ${bb_eqp_general_notes ¦ appearance:"multiline"}. Base Building Equipment Bonding Issues. ${bb_eqp_general_issues ¦ appearance:"multiline"}. How many pieces need bonding to the MPGP's ${bb_eqp_to_mpgp}; How many pieces need bonding to the SPGP's ${bb_eqp_to_spgp}; Cable tray needs bonded at the ends ${bb_eqp_cable_tray}. Junction boxes ${bb_eqp_jct_box}; E/G ${bb_eqp_eg}; ATS ${bb_eqp_ats}. SPD ${bb_eqp_spd}; Battery/UPS rack ${bb_eqp_batt_ups}; Conduits ${bb_eqp_conduits}. |
| --- | --- |

| 11.0 | INTERIOR UPS BUILDING |
| --- | --- |

| 11.1 | Interior MPG System |
| --- | --- |

|  | Does the facility have Main Ground Plate? ${ups_mpg ¦ checked:"yes"} Yes ${ups_mpg ¦ checked:"no"} No; Is it correct? ${ups_mpg_correct ¦ checked:"yes"} Yes ${ups_mpg_correct ¦ checked:"no"} No. UPS Building MPG Photos. ${# ups_mpg_photos}${$file ¦ size:0:0:560:380}${/}. UPS Building MPG Notes. ${ups_mpg_general_notes ¦ appearance:"multiline"}. UPS Building MPG Issues. ${ups_mpg_general_issues ¦ appearance:"multiline"}. Needs label changed ${ups_mpg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${ups_mpg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${ups_mpg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${ups_mpg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${ups_mpg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 11.2 | Supplemental Ground Plate |
| --- | --- |

|  | Does the facility have Supplemental Ground Plate? ${ups_spg ¦ checked:"yes"} Yes ${ups_spg ¦ checked:"no"} No; Is it correct? ${ups_spg_correct ¦ checked:"yes"} Yes ${ups_spg_correct ¦ checked:"no"} No. UPS Building SPG Photos. ${# ups_spg_photos}${$file ¦ size:0:0:560:380}${/}. UPS Building SPG Notes. ${ups_spg_general_notes ¦ appearance:"multiline"}. UPS Building SPG Issues. ${ups_spg_general_issues ¦ appearance:"multiline"}. Needs label changed ${ups_spg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${ups_spg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${ups_spg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${ups_spg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${ups_spg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 11.3 | MPGP |
| --- | --- |

|  | Does the facility have MPGP's? ${ups_mpgp ¦ checked:"yes"} Yes ${ups_mpgp ¦ checked:"no"} No; UPS Building MPGP Count ${ups_mpgp_count}; Are they correct? ${ups_mpgp_correct ¦ checked:"yes"} Yes ${ups_mpgp_correct ¦ checked:"no"} No. UPS Building MPGP Photos. ${# ups_mpgp_photos}${$file ¦ size:0:0:560:380}${/}. UPS Building MPGP Notes. ${ups_mpgp_general_notes ¦ appearance:"multiline"}. UPS Building MPGP Issues. ${ups_mpgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${ups_mpgp_label ¦ checked:"yes"} Yes; Undersized ${ups_mpgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${ups_mpgp_to_double_lug ¦ checked:"yes"} Yes. Needs interconnected with 4/0 to MPGP ${ups_mpgp_interconnect ¦ checked:"yes"} Yes; Need to add additional MPGP's ${ups_mpgp_add_count}; Wrong equipment bonded to MPGP ${ups_mpgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 11.4 | SPGP |
| --- | --- |

|  | Does the facility have SPGP's? ${ups_spgp ¦ checked:"yes"} Yes ${ups_spgp ¦ checked:"no"} No; UPS Building SPGP Count ${ups_spgp_count}; Are they correct? ${ups_spgp_correct ¦ checked:"yes"} Yes ${ups_spgp_correct ¦ checked:"no"} No. UPS Building SPGP Photos. ${# ups_spgp_photos}${$file ¦ size:0:0:560:380}${/}. UPS Building SPGP Notes. ${ups_spgp_general_notes ¦ appearance:"multiline"}. UPS Building SPGP Issues. ${ups_spgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${ups_spgp_label ¦ checked:"yes"} Yes; Undersized ${ups_spgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${ups_spgp_to_double_lug ¦ checked:"yes"} Yes. Is incorrectly interconnected with the MPG System (remove the interconnections) ${ups_spgp_inter_mpg ¦ checked:"yes"} Yes; Interconnection with Main/Supp needed with 4/0 ${ups_spgp_interconnect ¦ checked:"yes"} Yes; Need to add additional SPGP's ${ups_spgp_add_count}. Wrong equipment bonded to SPGP ${ups_spgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 11.5 | Interior Equipment Bonding |
| --- | --- |

|  | Does the facility have equipment that needs bonded to the MPG System? ${ups_eqp_bonds ¦ checked:"yes"} Yes ${ups_eqp_bonds ¦ checked:"no"} No; How many? ${ups_eqp_bonds_count}; Is the equipment bonded to the MPG System? ${ups_eqp_bond_mpg ¦ checked:"yes"} Yes ${ups_eqp_bond_mpg ¦ checked:"no"} No. How many? ${ups_eqp_bond_mpg_count}. UPS Building Equipment Bonding Photos. ${# ups_eqp_photos}${$file ¦ size:0:0:560:380}${/}. UPS Building Equipment Bonding Notes. ${ups_eqp_general_notes ¦ appearance:"multiline"}. UPS Building Equipment Bonding Issues. ${ups_eqp_general_issues ¦ appearance:"multiline"}. How many pieces need bonding to the MPGP's ${ups_eqp_to_mpgp}; How many pieces need bonding to the SPGP's ${ups_eqp_to_spgp}; Cable tray needs bonded at the ends ${ups_eqp_cable_tray}. Junction boxes ${ups_eqp_jct_box}; E/G ${ups_eqp_eg}; ATS ${ups_eqp_ats}. SPD ${ups_eqp_spd}; Battery/UPS rack ${ups_eqp_batt_ups}; Conduits ${ups_eqp_conduits}. |
| --- | --- |

| 12.0 | UPS ROOM |
| --- | --- |

| 12.1 | Interior MPG System |
| --- | --- |

|  | Does the facility have Main Ground Plate? ${ups_rm_mpg ¦ checked:"yes"} Yes ${ups_rm_mpg ¦ checked:"no"} No; Is it correct? ${ups_rm_mpg_correct ¦ checked:"yes"} Yes ${ups_rm_mpg_correct ¦ checked:"no"} No. UPS Room MPG Photos. ${# ups_rm_mpg_photos}${$file ¦ size:0:0:560:380}${/}. UPS Room MPG Notes. ${ups_rm_mpg_general_notes ¦ appearance:"multiline"}. UPS Room MPG Issues. ${ups_rm_mpg_general_issues ¦ appearance:"multiline"}. Needs label changed ${ups_rm_mpg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${ups_rm_mpg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${ups_rm_mpg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${ups_rm_mpg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${ups_rm_mpg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 12.2 | Supplemental Ground Plate |
| --- | --- |

|  | Does the facility have Supplemental Ground Plate? ${ups_rm_spg ¦ checked:"yes"} Yes ${ups_rm_spg ¦ checked:"no"} No; Is it correct? ${ups_rm_spg_correct ¦ checked:"yes"} Yes ${ups_rm_spg_correct ¦ checked:"no"} No. UPS Room SPG Photos. ${# ups_rm_spg_photos}${$file ¦ size:0:0:560:380}${/}. UPS Room SPG Notes. ${ups_rm_spg_general_notes ¦ appearance:"multiline"}. UPS Room SPG Issues. ${ups_rm_spg_general_issues ¦ appearance:"multiline"}. Needs label changed ${ups_rm_spg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${ups_rm_spg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${ups_rm_spg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${ups_rm_spg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${ups_rm_spg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 12.3 | MPGP |
| --- | --- |

|  | Does the facility have MPGP's? ${ups_rm_mpgp ¦ checked:"yes"} Yes ${ups_rm_mpgp ¦ checked:"no"} No; UPS Room MPGP Count ${ups_rm_mpgp_count}; Are they correct? ${ups_rm_mpgp_correct ¦ checked:"yes"} Yes ${ups_rm_mpgp_correct ¦ checked:"no"} No. UPS Room MPGP Photos. ${# ups_rm_mpgp_photos}${$file ¦ size:0:0:560:380}${/}. UPS Room MPGP Notes. ${ups_rm_mpgp_general_notes ¦ appearance:"multiline"}. UPS Room MPGP Issues. ${ups_rm_mpgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${ups_rm_mpgp_label ¦ checked:"yes"} Yes; Undersized ${ups_rm_mpgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${ups_rm_mpgp_to_double_lug ¦ checked:"yes"} Yes. Needs interconnected with 4/0 to MPGP ${ups_rm_mpgp_interconnect ¦ checked:"yes"} Yes; Need to add additional MPGP's ${ups_rm_mpgp_add_count}; Wrong equipment bonded to MPGP ${ups_rm_mpgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 12.4 | SPGP |
| --- | --- |

|  | Does the facility have SPGP's? ${ups_rm_spgp ¦ checked:"yes"} Yes ${ups_rm_spgp ¦ checked:"no"} No; UPS Room SPGP Count ${ups_rm_spgp_count}; Are they correct? ${ups_rm_spgp_correct ¦ checked:"yes"} Yes ${ups_rm_spgp_correct ¦ checked:"no"} No. UPS Room SPGP Photos. ${# ups_rm_spgp_photos}${$file ¦ size:0:0:560:380}${/}. UPS Room SPGP Notes. ${ups_rm_spgp_general_notes ¦ appearance:"multiline"}. UPS Room SPGP Issues. ${ups_rm_spgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${ups_rm_spgp_label ¦ checked:"yes"} Yes; Undersized ${ups_rm_spgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${ups_rm_spgp_to_double_lug ¦ checked:"yes"} Yes. Is incorrectly interconnected with the MPG System (remove the interconnections) ${ups_rm_spgp_inter_mpg ¦ checked:"yes"} Yes; Interconnection with Main/Supp needed with 4/0 ${ups_rm_spgp_interconnect ¦ checked:"yes"} Yes; Need to add additional SPGP's ${ups_rm_spgp_add_count}. Wrong equipment bonded to SPGP ${ups_rm_spgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 12.5 | Interior Equipment Bonding |
| --- | --- |

|  | Does the facility have equipment that needs bonded to the MPG System? ${ups_rm_eqp_bonds ¦ checked:"yes"} Yes ${ups_rm_eqp_bonds ¦ checked:"no"} No; How many? ${ups_rm_eqp_bonds_count}; Is the equipment bonded to the MPG System? ${ups_rm_eqp_bond_mpg ¦ checked:"yes"} Yes ${ups_rm_eqp_bond_mpg ¦ checked:"no"} No. How many? ${ups_rm_eqp_bond_mpg_count}. UPS Building Equipment Bonding Photos. ${# ups_rm_eqp_photos}${$file ¦ size:0:0:560:380}${/}. UPS Building Equipment Bonding Notes. ${ups_rm_eqp_general_notes ¦ appearance:"multiline"}. UPS Building Equipment Bonding Issues. ${ups_rm_eqp_general_issues ¦ appearance:"multiline"}. How many pieces need bonding to the MPGP's ${ups_rm_eqp_to_mpgp}; How many pieces need bonding to the SPGP's ${ups_rm_eqp_to_spgp}; Cable tray needs bonded at the ends ${ups_rm_eqp_cable_tray}. Junction boxes ${ups_rm_eqp_jct_box}; E/G ${ups_rm_eqp_eg}; ATS ${ups_rm_eqp_ats}. SPD ${ups_rm_eqp_spd}; Battery/UPS rack ${ups_rm_eqp_batt_ups}; Conduits ${ups_rm_eqp_conduits}. |
| --- | --- |

| 13.0 | INTERIOR EG BUILDING |
| --- | --- |

| 13.1 | Interior MPG System |
| --- | --- |

|  | Does the facility have Main Ground Plate? ${eg_mpg ¦ checked:"yes"} Yes ${eg_mpg ¦ checked:"no"} No; Is it correct? ${eg_mpg_correct ¦ checked:"yes"} Yes ${eg_mpg_correct ¦ checked:"no"} No. EG Building MPG Photos. ${# eg_mpg_photos}${$file ¦ size:0:0:560:380}${/}. EG Building MPG Notes. ${eg_mpg_general_notes ¦ appearance:"multiline"}. EG Building MPG Issues. ${eg_mpg_general_issues ¦ appearance:"multiline"}. Needs label changed ${eg_mpg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${eg_mpg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${eg_mpg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${eg_mpg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${eg_mpg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 13.2 | Supplemental Ground Plate |
| --- | --- |

|  | Does the facility have Supplemental Ground Plate? ${eg_spg ¦ checked:"yes"} Yes ${eg_spg ¦ checked:"no"} No; Is it correct? ${eg_spg_correct ¦ checked:"yes"} Yes ${eg_spg_correct ¦ checked:"no"} No. EG Building SPG Photos. ${# eg_spg_photos}${$file ¦ size:0:0:560:380}${/}. EG Building SPG Notes. ${eg_spg_general_notes ¦ appearance:"multiline"}. EG Building SPG Issues. ${eg_spg_general_issues ¦ appearance:"multiline"}. Needs label changed ${eg_spg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${eg_spg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${eg_spg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${eg_spg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${eg_spg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 13.3 | MPGP |
| --- | --- |

|  | Does the facility have MPGP's? ${eg_mpgp ¦ checked:"yes"} Yes ${eg_mpgp ¦ checked:"no"} No; EG Building MPGP Count ${eg_mpgp_count}; Are they correct? ${eg_mpgp_correct ¦ checked:"yes"} Yes ${eg_mpgp_correct ¦ checked:"no"} No. EG Building MPGP Photos. ${# eg_mpgp_photos}${$file ¦ size:0:0:560:380}${/}. EG Building MPGP Notes. ${eg_mpgp_general_notes ¦ appearance:"multiline"}. EG Building MPGP Issues. ${eg_mpgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${eg_mpgp_label ¦ checked:"yes"} Yes; Undersized ${eg_mpgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${eg_mpgp_to_double_lug ¦ checked:"yes"} Yes. Needs interconnected with 4/0 to MPGP ${eg_mpgp_interconnect ¦ checked:"yes"} Yes; Need to add additional MPGP's ${eg_mpgp_add_count}; Wrong equipment bonded to MPGP ${eg_mpgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 13.4 | SPGP |
| --- | --- |

|  | Does the facility have SPGP's? ${eg_spgp ¦ checked:"yes"} Yes ${eg_spgp ¦ checked:"no"} No; EG Building SPGP Count ${eg_spgp_count}; Are they correct? ${eg_spgp_correct ¦ checked:"yes"} Yes ${eg_spgp_correct ¦ checked:"no"} No. EG Building SPGP Photos. ${# eg_spgp_photos}${$file ¦ size:0:0:560:380}${/}. EG Building SPGP Notes. ${eg_spgp_general_notes ¦ appearance:"multiline"}. EG Building SPGP Issues. ${eg_spgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${eg_spgp_label ¦ checked:"yes"} Yes; Undersized ${eg_spgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${eg_spgp_to_double_lug ¦ checked:"yes"} Yes. Is incorrectly interconnected with the MPG System (remove the interconnections) ${eg_spgp_inter_mpg ¦ checked:"yes"} Yes; Interconnection with Main/Supp needed with 4/0 ${eg_spgp_interconnect ¦ checked:"yes"} Yes; Need to add additional SPGP's ${eg_spgp_add_count}. Wrong equipment bonded to SPGP ${eg_spgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 13.5 | Interior Equipment Bonding |
| --- | --- |

|  | Does the facility have equipment that needs bonded to the MPG System? ${eg_eqp_bonds ¦ checked:"yes"} Yes ${eg_eqp_bonds ¦ checked:"no"} No; How many? ${eg_eqp_bonds_count}; Is the equipment bonded to the MPG System? ${eg_eqp_bond_mpg ¦ checked:"yes"} Yes ${eg_eqp_bond_mpg ¦ checked:"no"} No. How many? ${eg_eqp_bond_mpg_count}. EG Building Equipment Bonding Photos. ${# eg_eqp_photos}${$file ¦ size:0:0:560:380}${/}. EG Building Equipment Bonding Notes. ${eg_eqp_general_notes ¦ appearance:"multiline"}. EG Building Equipment Bonding Issues. ${eg_eqp_general_issues ¦ appearance:"multiline"}. How many pieces need bonding to the MPGP's ${eg_eqp_to_mpgp}; How many pieces need bonding to the SPGP's ${eg_eqp_to_spgp}; Cable tray needs bonded at the ends ${eg_eqp_cable_tray}. Junction boxes ${eg_eqp_jct_box}; E/G ${eg_eqp_eg}; ATS ${eg_eqp_ats}. SPD ${eg_eqp_spd}; Battery/UPS rack ${eg_eqp_batt_ups}; Conduits ${eg_eqp_conduits}. |
| --- | --- |

| 14.0 | EG ROOM |
| --- | --- |

| 14.1 | Interior MPG System |
| --- | --- |

|  | Does the facility have Main Ground Plate? ${eg_rm_mpg ¦ checked:"yes"} Yes ${eg_rm_mpg ¦ checked:"no"} No; Is it correct? ${eg_rm_mpg_correct ¦ checked:"yes"} Yes ${eg_rm_mpg_correct ¦ checked:"no"} No. EG Room MPG Photos. ${# eg_rm_mpg_photos}${$file ¦ size:0:0:560:380}${/}. EG Room MPG Notes. ${eg_rm_mpg_general_notes ¦ appearance:"multiline"}. EG Room MPG Issues. ${eg_rm_mpg_general_issues ¦ appearance:"multiline"}. Needs label changed ${eg_rm_mpg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${eg_rm_mpg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${eg_rm_mpg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${eg_rm_mpg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${eg_rm_mpg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 14.2 | Supplemental Ground Plate |
| --- | --- |

|  | Does the facility have Supplemental Ground Plate? ${eg_rm_spg ¦ checked:"yes"} Yes ${eg_rm_spg ¦ checked:"no"} No; Is it correct? ${eg_rm_spg_correct ¦ checked:"yes"} Yes ${eg_rm_spg_correct ¦ checked:"no"} No. EG Room SPG Photos. ${# eg_rm_spg_photos}${$file ¦ size:0:0:560:380}${/}. EG Room SPG Notes. ${eg_rm_spg_general_notes ¦ appearance:"multiline"}. EG Room SPG Issues. ${eg_rm_spg_general_issues ¦ appearance:"multiline"}. Needs label changed ${eg_rm_spg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${eg_rm_spg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${eg_rm_spg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${eg_rm_spg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${eg_rm_spg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 14.3 | MPGP |
| --- | --- |

|  | Does the facility have MPGP's? ${eg_rm_mpgp ¦ checked:"yes"} Yes ${eg_rm_mpgp ¦ checked:"no"} No; EG Room MPGP Count ${eg_rm_mpgp_count}; Are they correct? ${eg_rm_mpgp_correct ¦ checked:"yes"} Yes ${eg_rm_mpgp_correct ¦ checked:"no"} No. EG Room MPGP Photos. ${# eg_rm_mpgp_photos}${$file ¦ size:0:0:560:380}${/}. EG Room MPGP Notes. ${eg_rm_mpgp_general_notes ¦ appearance:"multiline"}. EG Room MPGP Issues. ${eg_rm_mpgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${eg_rm_mpgp_label ¦ checked:"yes"} Yes; Undersized ${eg_rm_mpgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${eg_rm_mpgp_to_double_lug ¦ checked:"yes"} Yes. Needs interconnected with 4/0 to MPGP ${eg_rm_mpgp_interconnect ¦ checked:"yes"} Yes; Need to add additional MPGP's ${eg_rm_mpgp_add_count}; Wrong equipment bonded to MPGP ${eg_rm_mpgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 14.4 | SPGP |
| --- | --- |

|  | Does the facility have SPGP's? ${eg_rm_spgp ¦ checked:"yes"} Yes ${eg_rm_spgp ¦ checked:"no"} No; EG Room SPGP Count ${eg_rm_spgp_count}; Are they correct? ${eg_rm_spgp_correct ¦ checked:"yes"} Yes ${eg_rm_spgp_correct ¦ checked:"no"} No. EG Room SPGP Photos. ${# eg_rm_spgp_photos}${$file ¦ size:0:0:560:380}${/}. EG Room SPGP Notes. ${eg_rm_spgp_general_notes ¦ appearance:"multiline"}. EG Room SPGP Issues. ${eg_rm_spgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${eg_rm_spgp_label ¦ checked:"yes"} Yes; Undersized ${eg_rm_spgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${eg_rm_spgp_to_double_lug ¦ checked:"yes"} Yes. Is incorrectly interconnected with the MPG System (remove the interconnections) ${eg_rm_spgp_inter_mpg ¦ checked:"yes"} Yes; Interconnection with Main/Supp needed with 4/0 ${eg_rm_spgp_interconnect ¦ checked:"yes"} Yes; Need to add additional SPGP's ${eg_rm_spgp_add_count}. Wrong equipment bonded to SPGP ${eg_rm_spgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 14.5 | Interior Equipment Bonding |
| --- | --- |

|  | Does the facility have equipment that needs bonded to the MPG System? ${eg_rm_eqp_bonds ¦ checked:"yes"} Yes ${eg_rm_eqp_bonds ¦ checked:"no"} No; How many? ${eg_rm_eqp_bonds_count}; Is the equipment bonded to the MPG System? ${eg_rm_eqp_bond_mpg ¦ checked:"yes"} Yes ${eg_rm_eqp_bond_mpg ¦ checked:"no"} No. How many? ${eg_rm_eqp_bond_mpg_count}. EG Room Equipment Bonding Photos. ${# eg_rm_eqp_photos}${$file ¦ size:0:0:560:380}${/}. EG Room Equipment Bonding Notes. ${eg_rm_eqp_general_notes ¦ appearance:"multiline"}. EG Room Equipment Bonding Issues. ${eg_rm_eqp_general_issues ¦ appearance:"multiline"}. How many pieces need bonding to the MPGP's ${eg_rm_eqp_to_mpgp}; How many pieces need bonding to the SPGP's ${eg_rm_eqp_to_spgp}; Cable tray needs bonded at the ends ${eg_rm_eqp_cable_tray}. Junction boxes ${eg_rm_eqp_jct_box}; E/G ${eg_rm_eqp_eg}; ATS ${eg_rm_eqp_ats}. SPD ${eg_rm_eqp_spd}; Battery/UPS rack ${eg_rm_eqp_batt_ups}; Conduits ${eg_rm_eqp_conduits}. |
| --- | --- |

| 15.0 | INTERIOR OTHER |
| --- | --- |

| 15.1 | Interior MPG System |
| --- | --- |

|  | Does the facility have Main Ground Plate? ${other_mpg ¦ checked:"yes"} Yes ${other_mpg ¦ checked:"no"} No; Is it correct? ${other_mpg_correct ¦ checked:"yes"} Yes ${other_mpg_correct ¦ checked:"no"} No. Other MPG Photos. ${# other_mpg_photos}${$file ¦ size:0:0:560:380}${/}. Other MPG Notes. ${other_mpg_general_notes ¦ appearance:"multiline"}. Other MPG Issues. ${other_mpg_general_issues ¦ appearance:"multiline"}. Needs label changed ${other_mpg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${other_mpg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${other_mpg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${other_mpg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${other_mpg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 15.2 | Supplemental Ground Plate |
| --- | --- |

|  | Does the facility have Supplemental Ground Plate? ${other_spg ¦ checked:"yes"} Yes ${other_spg ¦ checked:"no"} No; Is it correct? ${other_spg_correct ¦ checked:"yes"} Yes ${other_spg_correct ¦ checked:"no"} No. Other SPG Photos. ${# other_spg_photos}${$file ¦ size:0:0:560:380}${/}. Other SPG Notes. ${other_spg_general_notes ¦ appearance:"multiline"}. Other SPG Issues. ${other_spg_general_issues ¦ appearance:"multiline"}. Needs label changed ${other_spg_label ¦ checked:"yes"} Yes; Needs 500 mcm or 4/0 to EES ${other_spg_bond_to_ees ¦ checked:"yes"} Yes; Undersized ${other_spg_undersized ¦ checked:"yes"} Yes. Convert to double lug terminals ${other_spg_to_double_lug ¦ checked:"yes"} Yes; Needs interconnected with 4/0 to MPGP ${other_spg_interconnect ¦ checked:"yes"} Yes. |
| --- | --- |

| 15.3 | MPGP |
| --- | --- |

|  | Does the facility have MPGP's? ${other_mpgp ¦ checked:"yes"} Yes ${other_mpgp ¦ checked:"no"} No; Other MPGP Count ${other_mpgp_count}; Are they correct? ${other_mpgp_correct ¦ checked:"yes"} Yes ${other_mpgp_correct ¦ checked:"no"} No. Other MPGP Photos. ${# other_mpgp_photos}${$file ¦ size:0:0:560:380}${/}. Other MPGP Notes. ${other_mpgp_general_notes ¦ appearance:"multiline"}. Other MPGP Issues. ${other_mpgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${other_mpgp_label ¦ checked:"yes"} Yes; Undersized ${other_mpgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${other_mpgp_to_double_lug ¦ checked:"yes"} Yes. Needs interconnected with 4/0 to MPGP ${other_mpgp_interconnect ¦ checked:"yes"} Yes; Need to add additional MPGP's ${other_mpgp_add_count}; Wrong equipment bonded to MPGP ${other_mpgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 15.4 | SPGP |
| --- | --- |

|  | Does the facility have SPGP's? ${other_spgp ¦ checked:"yes"} Yes ${other_spgp ¦ checked:"no"} No; Other SPGP Count ${other_spgp_count}; Are they correct? ${other_spgp_correct ¦ checked:"yes"} Yes ${other_spgp_correct ¦ checked:"no"} No. Other SPGP Photos. ${# other_spgp_photos}${$file ¦ size:0:0:560:380}${/}. Other SPGP Notes. ${other_spgp_general_notes ¦ appearance:"multiline"}. Other SPGP Issues. ${other_spgp_general_issues ¦ appearance:"multiline"}. Needs label changed ${other_spgp_label ¦ checked:"yes"} Yes; Undersized ${other_spgp_undersized ¦ checked:"yes"} Yes; Convert to double lug terminals ${other_spgp_to_double_lug ¦ checked:"yes"} Yes. Is incorrectly interconnected with the MPG System (remove the interconnections) ${other_spgp_inter_mpg ¦ checked:"yes"} Yes; Interconnection with Main/Supp needed with 4/0 ${other_spgp_interconnect ¦ checked:"yes"} Yes; Need to add additional SPGP's ${other_spgp_add_count}. Wrong equipment bonded to SPGP ${other_spgp_wrong_bonds ¦ checked:"yes"} Yes. |
| --- | --- |

| 15.5 | Interior Equipment Bonding |
| --- | --- |

|  | Does the facility have equipment that needs bonded to the MPG System? ${other_eqp_bonds ¦ checked:"yes"} Yes ${other_eqp_bonds ¦ checked:"no"} No; How many? ${other_eqp_bonds_count}; Is the equipment bonded to the MPG System? ${other_eqp_bond_mpg ¦ checked:"yes"} Yes ${other_eqp_bond_mpg ¦ checked:"no"} No. How many? ${other_eqp_bond_mpg_count}. Other Equipment Bonding Photos. ${# other_eqp_photos}${$file ¦ size:0:0:560:380}${/}. Other Equipment Bonding Notes. ${other_eqp_general_notes ¦ appearance:"multiline"}. Other Equipment Bonding Issues. ${other_eqp_general_issues ¦ appearance:"multiline"}. How many pieces need bonding to the MPGP's ${other_eqp_to_mpgp}; How many pieces need bonding to the SPGP's ${other_eqp_to_spgp}; Cable tray needs bonded at the ends ${other_eqp_cable_tray}. Junction boxes ${other_eqp_jct_box}; E/G ${other_eqp_other}; ATS ${other_eqp_ats}. SPD ${other_eqp_spd}; Battery/UPS rack ${other_eqp_batt_ups}; Conduits ${other_eqp_conduits}. |
| --- | --- |

| 16.0 | SURGE PROTECTIVE DEVICES |
| --- | --- |

REPEAT RECORDS - SURGE PROTECTIVE DEVICES INSPECTION

| ${# SURGE_PROTECTIVE_DEVICES} |  |
| --- | --- |
| RECORD ${$position} ¦ Surge Protective Devices Inspection |  |
| Field | Response |
| Details |  |
| Choose Facility Location | ${spd_section_selector} |
| Describe the Location | ${spd_location_description} |
| Floor # | ${floor_number} |
| Room # | ${room_number} |
| SPD General Photos | ${# spd_images}${$file ¦ size:0:0:560:380}${/} |
| SPD General Notes | ${spd_general_notes ¦ appearance:"multiline"} |
| SPD General Issues | ${spd_general_issues ¦ appearance:"multiline"} |
| Surge Protective Devices |  |
| Is this a service entrance/first point of entry to facility/transfer switch or feeder panel? | ${spd_poe ¦ checked:"Service Entrance"} Service Entrance ${spd_poe ¦ checked:"Feeder Panel"} Feeder Panel |
| What is the voltage? | ${spd_voltage} |
| Is there currently an SPD installed? | ${spd_installed ¦ checked:"yes"} Yes ${spd_installed ¦ checked:"no"} No ${spd_installed ¦ checked:"n/a"} N/A |
| What is the amperage of the panel? | ${spd_amp} |
| Panel Label | ${spd_label} |
| Is there an existing breaker or disconnect? | ${spd_break_disc ¦ checked:"yes"} Yes ${spd_break_disc ¦ checked:"no"} No ${spd_break_disc ¦ checked:"n/a"} N/A |
| If so, what size? | ${spd_break_disc_size} |
| If not, is there room in the panel for another breaker? | ${spd_break_disc_room ¦ checked:"yes"} Yes ${spd_break_disc_room ¦ checked:"no"} No ${spd_break_disc_room ¦ checked:"n/a"} N/A |
| Describe setup | ${spd_break_disc_notes ¦ appearance:"multiline"} |
| Recommended SPD Model | ${spd_model} |
| SPD Photo | ${# spd_photo}${$file ¦ size:0:0:560:380}${/} |
| ${/} |  |

| 17.0 | SUBMIT SURVEY |
| --- | --- |

| 17.1 | Submitting Your Survey |
| --- | --- |

|  | Survey Date ${survey_date ¦ format:"MM/DD/YYYY"}. |
| --- | --- |

| S.0 | SIGN-OFF |
| --- | --- |

|  | Inspector ${creator}; Date Completed ${$feature ¦ getValue:"" ¦ format:"MM/DD/YYYY"}. Reviewer; Notes. |
| --- | --- |